## Baseline Calculation
PV SIZING
Daily Power | 59.8 | kW/day
Energy Demand | 561 | kWh/day
Sh | 3.24 | h (July)
fd | 75 | (%) Derating Factor
Module Power | 585 | Wp @STC
fd | 75 | %
PV Capacity | 230.8642 | kW
Nmodules | 394.6397 | Total
Nmod/s -min | 10.8548 | PV- minimum series connection
Nmod/s -max | 14.4731 | PV - maximum series connection
Nmod/s | 12 | PV- System Series connection
Nstrings | 32.8866 | PV- System Parallel connection
Total Panel | 394.6397 | Total PV System Panels
Panel Power (kW) | 230.8642 | kW
Battery Connections | 30 | Series connection
Inverter | 74.75 | kW Inverter minmum norminal power
Inverter Input voltage range | 480V - 680V
Vin (min) | 480 | V
Vin (max) | 640 | V
Module Vmp | 44.22 | V
Module Imp | 13.23 | A
Voc | 53.42 | V (Open-circuit voltage)
Isc | 13.91 | A (Short-circuit current)
DA (Days) | Battery Capacity | Unit | Battery in Parallel | Total Battery
1 | 340206.1856 | Ah | 113.4021 | 3402.0619
Battery Sizing Parameters | Value | Unit | Remark
Tc | 10 | % | Safety Margin
DA | 1 | day | Days of Autonomy
DM | 10 | % | Design Margin
DOD | 85 | % | Degree of Discharge
Vbat | 2 | V | Nominal Voltage
Beff | 97 | % | Battery Efficiency
System Voltage | 60 | V
Battery Capacity | 3000 | Ah
Month | E_Avalable (kWh) | E_User (kWh) | E_Unused (kWh) | E_Losses (kWh) | E_Missing (Unmet) (kWh) | E_Load (KWh) | Solar Fraction | Performance Ratio
January | 33852 | 17391 | 14884 | 1577 | 0 | 17391 | 1 | 44%
February | 30233 | 15708 | 13820 | 705 | 0 | 15708 | 1 | 45%
March | 29995 | 17391 | 12434 | 170 | 0 | 17391 | 1 | 50%
April | 27249 | 16830 | 9047 | 1372 | 0 | 16830 | 1 | 52%
May | 25516 | 17391 | 7697 | 428 | 0 | 17391 | 1 | 57%
June | 20371 | 16830 | 3210 | 331 | 0 | 16830 | 1 | 70%
July | 19274 | 17391 | 2549 | 666 | 0 | 17391 | 1 | 75.5%
August | 20714 | 16466 | 2049 | 2199 | 925 | 17391 | 0.947 | 66%
September | 20318 | 15457 | 4226 | 635 | 1274 | 16830 | 0.918 | 63%
October | 22744 | 17391 | 4887 | 466 | 0 | 17391 | 1 | 63%
November | 25955 | 16830 | 8688 | 437 | 0 | 16830 | 1 | 51.5%
December | 32517 | 17391 | 13890 | 1236 | 0 | 17391 | 1 | 40%
| Sum | 202467 |  |  |  |  | Average | 56.42%
New simulation variant - Commercial Centre 2
Customised table
Month | EBatDis | EBatCh | UBatDis | IBatDis | OutConv | CnvLoss | Coverter Energy | Instant battery Output to User | Instant PV Output to User
Unit | kWh | kWh | V | Ah | kWh | kWh | kWh | kWh | kWh
January | 10609 | 12101 | 63.8 | 166106 | 18968 | 814 | 19782 | 10172.4554 | 7218.5446
February | 9940 | 10557 | 63.8 | 155578.7 | 16413 | 736 | 17149 | 9513.3955 | 6194.6045
March | 10564 | 10659 | 63.8 | 165488.4 | 17561 | 835 | 18396 | 10084.4968 | 7306.5032
April | 9033 | 10351 | 63.6 | 141750.8 | 18202 | 859 | 19061 | 8625.9203 | 8204.0797
May | 9106 | 9484 | 63.7 | 142752.8 | 17819 | 850 | 18669 | 8691.4036 | 8699.5964
June | 8469 | 8771 | 63.4 | 133598.1 | 17160 | 950 | 18110 | 8024.7399 | 8805.2601
July | 8645 | 7952 | 63.1 | 136988.7 | 16726 | 997 | 17723 | 8158.6791 | 9232.3209
August | 7518 | 9690 | 63.1 | 118824.1 | 18664 | 1010 | 19674 | 7132.05 | 9333.95
September | 8028 | 8627 | 63 | 127007.9 | 16092 | 921 | 17013 | 7593.4036 | 7863.5964
October | 8814 | 9242 | 63.1 | 139532.1 | 17857 | 996 | 18853 | 8348.3582 | 9042.6418
November | 9412 | 9791 | 63.7 | 147562.2 | 17267 | 857 | 18124 | 8966.9501 | 7863.0499
December | 10948 | 12101 | 63.8 | 171356.6 | 18627 | 755 | 19382 | 10521.5352 | 6869.4648
Year | 111085 | 119325 | 63.5 | 1746546.4 | 211356 | 10580 | 221936 | 105789.4224 | 96677.5776
Hour | Daily Load Profile (kW) | Hourly Average Load (kW) - Best Month | Hourly Average Load (kW) - Worst Month | Hourly Average Load (kW) - Yearly Average
0:00 | 9 | 8.8 | 7.9 | 8.7
1:00 | 9 | 8.8 | 7.9 | 8.7
2:00 | 9 | 8.8 | 7.9 | 8.7
3:00 | 9 | 8.8 | 7.9 | 8.7
4:00 | 9 | 8.8 | 7.9 | 8.7
5:00 | 9 | 8.8 | 7.9 | 8.7
6:00 | 9 | 8.8 | 7.9 | 8.7
7:00 | 9 | 8.8 | 7.9 | 8.7
8:00 | 21 | 21.3 | 19.1 | 21
9:00 | 33.5 | 35.1 | 31.6 | 34.7
10:00 | 47 | 46.4 | 42 | 45.8
11:00 | 47 | 46.4 | 43.3 | 45.9
12:00 | 47 | 46.4 | 43.3 | 46
13:00 | 45 | 45 | 42 | 44.6
14:00 | 33.5 | 33.7 | 31.5 | 33.4
15:00 | 33.5 | 33.7 | 31.5 | 33.4
16:00 | 33.5 | 33.7 | 31.5 | 33.4
17:00 | 33.5 | 33.7 | 31.5 | 33.4
18:00 | 33.5 | 33.7 | 32.4 | 33.3
19:00 | 21 | 21.3 | 19.1 | 21
20:00 | 21 | 21.3 | 19.1 | 21
21:00 | 21 | 21.3 | 19.2 | 21
22:00 | 9 | 8.8 | 7.9 | 8.7
23:00 | 9 | 8.8 | 7.9 | 8.7
|  | Best Month | February
|  | Worst Month | July

## Sensitivity Analysis
Inverter
Daily Power | 59.8 | kW/day |  | Input voltage range |  |  |  | Connection Configuration
Energy Demand | 561 | kWh/day |  | Vin (min) | 480 | V |  | Voc | 53.42 | V
Sh | 4.21 | h (Average) |  | Vin (max) | 640 | V |  | Ioc | 13.91 | A
fd | 75 | % (Derating Factor) |  | Module Vmp | 44.22 | V
Module Power | 585 | Wp @STC |  | Module Imp | 13.23 | A
Parameters | fd | PV Capacity (kW) | Nmodules | Nmod/s (min) | Nmod/s (max) | Nmod/s | Nstrings | Total Panel | Panel Power (kW)
Value | 0.75 | 177.6722 | 303.7132 | 10.8548 | 14.4731 | 12 | 25.3094 | 303.7132 | 177.6722
Designs | Sh (h) | PV Capacity (kW) | Total Panel | User Energy Need (kWh/year) | Availabe Energy (kWh/year | Useful Energy (kWh/year) | Excess Energy (kWh/year) | Missing Energy | Performance Ratio (%) | Solar Fraction (%)
Baseline | 3.21 | 231 | 395 | 204765 | 308736 | 202467 | 97355 | 2299 | 56.4 | 98.9
Optimized | 4.21 | 178 | 304 | 204765 | 241630 | 196780 | 37436 | 7987 | 69.6 | 96.1

## PV Economic Analysis
PV Cost | 41699 | $
Battery Cost | 99000 | $
Discount rate | 8%
Tarrif rate | 0.2 | $
Initial Investment Cost | 152863.9 | $
Charge Controller | 1010 | $
Inverter Cost | 6985 | $
Installation/Logistics | 4169.9 | $
O&M Cost | 7643.195 | $
Battery Repl Cost | 103950 | $
Inverter Repl Cost | 7334.25
Unused Energy | 97381 | kWh/yr
[7 empty] | PRESENT VALUE | [5 empty] | BENEFITS
Year | Initial Investment cost | Cost (O&M) | Cost (Repl) | Cost (Other) | Cost (Salvage) | Energy (kWh) | Initial cost | Cost (O&M) | Cost (repl) | Cost (other) | Cost (salvage) | Energy kWh | Benefit | Present Value Benefit
0 | 152863.9 | [5 empty] | 152863.9 | 0 | 0 | 0 | 0 | 0
1 |  | 7643.195 |  |  |  | 202467 | 0 | 7077.0324 | 0 |  |  | 187469.4444 | 40493.4 | 37493.8889
2 |  | 7643.195 |  |  |  | 202467 | 0 | 6552.8078 | 0 |  |  | 173582.8189 | 40493.4 | 34716.5638
3 |  | 7643.195 |  |  |  | 202467 | 0 | 6067.4146 | 0 |  |  | 160724.8323 | 40493.4 | 32144.9665
4 |  | 7643.195 |  |  |  | 202467 | 0 | 5617.9765 | 0 |  |  | 148819.2892 | 40493.4 | 29763.8578
5 |  | 7643.195 |  |  |  | 202467 | 0 | 5201.8301 | 0 |  |  | 137795.6382 | 40493.4 | 27559.1276
6 |  | 7643.195 |  |  |  | 202467 | 0 | 4816.5093 | 0 |  |  | 127588.5538 | 40493.4 | 25517.7108
7 |  | 7643.195 |  |  |  | 202467 | 0 | 4459.7309 | 0 |  |  | 118137.5499 | 40493.4 | 23627.51
8 |  | 7643.195 |  |  |  | 202467 | 0 | 4129.3804 | 0 |  |  | 109386.6202 | 40493.4 | 21877.324
9 |  | 7643.195 |  |  |  | 202467 | 0 | 3823.5004 | 0 |  |  | 101283.9076 | 40493.4 | 20256.7815
10 |  | 7643.195 |  |  |  | 202467 | 0 | 3540.2782 | 0 |  |  | 93781.396 | 40493.4 | 18756.2792
11 |  | 7643.195 |  |  |  | 202467 | 0 | 3278.0353 | 0 |  |  | 86834.6259 | 40493.4 | 17366.9252
12 |  | 7643.195 |  |  |  | 202467 | 0 | 3035.2179 | 0 |  |  | 80402.4314 | 40493.4 | 16080.4863
13 |  | 7643.195 |  |  |  | 202467 | 0 | 2810.3869 | 0 |  |  | 74446.6957 | 40493.4 | 14889.3391
14 |  | 7643.195 |  |  |  | 202467 | 0 | 2602.2101 | 0 |  |  | 68932.1257 | 40493.4 | 13786.4251
15 |  | 7643.195 |  |  |  | 202467 | 0 | 2409.4538 | 0 |  |  | 63826.0423 | 40493.4 | 12765.2085
16 |  | 7643.195 | 111284.25 |  |  | 202467 | 0 | 2230.9758 | 32482.8118 |  |  | 59098.1873 | 40493.4 | 11819.6375
17 |  | 7643.195 |  |  |  | 202467 | 0 | 2065.7183 | 0 |  |  | 54720.5438 | 40493.4 | 10944.1088
18 |  | 7643.195 |  |  |  | 202467 | 0 | 1912.7021 | 0 |  |  | 50667.1702 | 40493.4 | 10133.434
19 |  | 7643.195 |  |  |  | 202467 | 0 | 1771.0205 | 0 |  |  | 46914.0465 | 40493.4 | 9382.8093
20 |  | 7643.195 |  |  |  | 202467 | 0 | 1639.8338 | 0 |  |  | 43438.9319 | 40493.4 | 8687.7864
21 |  | 7643.195 |  |  |  | 202467 | 0 | 1518.3646 | 0 |  |  | 40221.2332 | 40493.4 | 8044.2466
22 |  | 7643.195 |  |  |  | 202467 | 0 | 1405.8932 | 0 |  |  | 37241.8826 | 40493.4 | 7448.3765
23 |  | 7643.195 |  |  |  | 202467 | 0 | 1301.7529 | 0 |  |  | 34483.2247 | 40493.4 | 6896.6449
24 |  | 7643.195 |  |  |  | 202467 | 0 | 1205.3268 | 0 |  |  | 31928.9117 | 40493.4 | 6385.7823
25 |  | 7643.195 |  |  |  | 202467 | 0 | 1116.0433 | 0 |  |  | 29563.8072 | 40493.4 | 5912.7614
[7 empty] | 152863.9 | 81589.396 | 32482.8118 |  |  | 2161289.9106 |  | 432257.9821
LCOE | 0.12351 | kWh
Life Cycle Cost | 266936.1078 | $
Present Value Benefit | 432257.9821 | $
Net Present Value | 165321.8744 | $
IRR | 20.5 | %
Simple Payback | 3.775 | years
EXCESS ENERGY BENEFIT
Unsed Energy (kWh) | Present Value of Energy | Benefit
97381 | 81150.8333 | 16230.1667
97381 | 67625.6944 | 13525.1389
97381 | 56354.7454 | 11270.9491
97381 | 46962.2878 | 9392.4576
97381 | 39135.2398 | 7827.048
97381 | 32612.6999 | 6522.54
97381 | 27177.2499 | 5435.45
97381 | 22647.7082 | 4529.5416
97381 | 18873.0902 | 3774.618
97381 | 15727.5752 | 3145.515
97381 | 13106.3126 | 2621.2625
97381 | 10921.9272 | 2184.3854
97381 | 9101.606 | 1820.3212
97381 | 7584.6717 | 1516.9343
97381 | 6320.5597 | 1264.1119
97381 | 5267.1331 | 1053.4266
97381 | 4389.2776 | 877.8555
97381 | 3657.7313 | 731.5463
97381 | 3048.1094 | 609.6219
97381 | 2540.0912 | 508.0182
97381 | 2116.7427 | 423.3485
97381 | 1763.9522 | 352.7904
97381 | 1469.9602 | 293.992
97381 | 1224.9668 | 244.9934
97381 | 1020.8057 | 204.1611
| 481800.9716 | 96360.1943
Total Benefit | 2643090.8822 | $
LCOE | 0.10099 | kWh
Present Value Benefit | 528618.1764 | $
Net Present Value | 261682.0687 | $
Simple Pyaback | 1.2566 | year
IRR | 50.8 | %

## O&M_Sensitivity
Percentage Variability (%) | O&M Cost ($) | LCOE ($/kWh)
1 | 1528.639 | 0.1
3 | 4585.917 | 0.11
5 | 7643.195 | 0.12
7 | 10700.473 | 0.14
10 | 15286.39 | 0.16
12 | 18343.668 | 0.17
15 | 22929.585 | 0.19

## Diesel Gen. Economic Analysis
Cost of Generator | 58300 | $
Generator (Repl) | 52470 | $
Discount rate | 11.5%
Tarrif rate | 0.23 | $
Installation/Logistics | 5830 | $
O$M Cost | 58722.74 | $
[7 empty] | PRESENT VALUE | [5 empty] | BENEFIT
Year | Initial Investment cost | Cost (O&M) | Cost (Repl) | Cost (Other) | Cost (Salvage) | Energy (kWh) | Initial cost | Cost (O&M) | Cost (repl) | Cost (other) | Cost (salvage) | Energy kWh | Benefit | Present Value Benefit
0 | 64130 | [5 empty] | 64130 | 0 | 0 | 0 | 0 | 0
1 |  | 58722.74 |  |  |  | 204765 | 0 | 52666.1345 | 0 |  |  | 183645.7399 | 47095.95 | 42238.5202
2 |  | 58722.74 |  |  |  | 204765 | 0 | 47234.2014 | 0 |  |  | 164704.6995 | 47095.95 | 37882.0809
3 |  | 58722.74 |  |  |  | 204765 | 0 | 42362.5124 | 0 |  |  | 147717.2193 | 47095.95 | 33974.9604
4 |  | 58722.74 |  |  |  | 204765 | 0 | 37993.2847 | 0 |  |  | 132481.811 | 47095.95 | 30470.8165
5 |  | 58722.74 |  |  |  | 204765 | 0 | 34074.6948 | 0 |  |  | 118817.7677 | 47095.95 | 27328.0866
6 |  | 58722.74 | 58300 |  |  | 204765 | 0 | 30560.2644 | 30340.2637 |  |  | 106563.0204 | 47095.95 | 24509.4947
7 |  | 58722.74 |  |  |  | 204765 | 0 | 27408.3089 | 0 |  |  | 95572.2156 | 47095.95 | 21981.6096
8 |  | 58722.74 |  |  |  | 204765 | 0 | 24581.4429 | 0 |  |  | 85714.9915 | 47095.95 | 19714.4481
9 |  | 58722.74 |  |  |  | 204765 | 0 | 22046.1372 | 0 |  |  | 76874.4319 | 47095.95 | 17681.1193
10 |  | 58722.74 |  |  |  | 204765 | 0 | 19772.3203 | 0 |  |  | 68945.6788 | 47095.95 | 15857.5061
11 |  | 58722.74 |  |  |  | 204765 | 0 | 17733.0227 | 0 |  |  | 61834.6895 | 47095.95 | 14221.9786
12 |  | 58722.74 | 58300 |  |  | 204765 | 0 | 15904.0562 | 15789.5643 |  |  | 55457.1206 | 47095.95 | 12755.1377
13 |  | 58722.74 |  |  |  | 204765 | 0 | 14263.7276 | 0 |  |  | 49737.3279 | 47095.95 | 11439.5854
14 |  | 58722.74 |  |  |  | 204765 | 0 | 12792.5808 | 0 |  |  | 44607.469 | 47095.95 | 10259.7179
15 |  | 58722.74 |  |  |  | 204765 | 0 | 11473.1666 | 0 |  |  | 40006.6987 | 47095.95 | 9201.5407
16 |  | 58722.74 |  |  |  | 204765 | 0 | 10289.8355 | 0 |  |  | 35880.4472 | 47095.95 | 8252.5029
17 |  | 58722.74 |  |  |  | 204765 | 0 | 9228.552 | 0 |  |  | 32179.7733 | 47095.95 | 7401.3479
18 |  | 58722.74 | 58300 |  |  | 204765 | 0 | 8276.7283 | 8217.1448 |  |  | 28860.7832 | 47095.95 | 6637.9801
19 |  | 58722.74 |  |  |  | 204765 | 0 | 7423.0747 | 0 |  |  | 25884.1105 | 47095.95 | 5953.3454
20 |  | 58722.74 |  |  |  | 204765 | 0 | 6657.4661 | 0 |  |  | 23214.4489 | 47095.95 | 5339.3232
21 |  | 58722.74 |  |  |  | 204765 | 0 | 5970.8216 | 0 |  |  | 20820.1335 | 47095.95 | 4788.6307
22 |  | 58722.74 |  |  |  | 204765 | 0 | 5354.997 | 0 |  |  | 18672.7655 | 47095.95 | 4294.7361
23 |  | 58722.74 |  |  |  | 204765 | 0 | 4802.6879 | 0 |  |  | 16746.8749 | 47095.95 | 3851.7812
24 |  | 58722.74 | 58300 |  |  | 204765 | 0 | 4307.3434 | 4276.3352 |  |  | 15019.6187 | 47095.95 | 3454.5123
25 |  | 58722.74 |  |  |  | 204765 | 0 | 3863.0882 | 0 |  |  | 13470.5101 | 47095.95 | 3098.2173
[7 empty] | 64130 | 477040.4502 | 58623.308 |  |  | 1663430.3472 |  | 382588.9798
LCOE | 0.36058 | kWh
Life Cycle Cost | 599793.7582 | $
Present Value Benefit | 382588.9798 | $
Net Present Value | -217204.7783 | $
Simple Payback Time | 1.3617 | year
IRR | 2.1385e+12 | %

## Inverter Datasheet
Inverter Datasheet
Parameters | Value
Rated Power | 80kW
Peak Power | 240 kVA
Battery Voltage | 384 VDC
PV Input Voltage Range | 480V – 640V
Charging Current | 100A
Maximum PV Input Voltage | 800V
Inverter Type | Pure sine wave
Efficiency | >95%
Phase | 3/N/PE

## Energy_Power Use Calculation
MARKET SQUARE
Subject | Power Rating (W) | Quantity | Total Power (kW) | Daily Usage (h/day) | Energy (kWh/day)
Refrigeration – back freezer | 1125 | 2 | 2.25 | 24 | 54
Refrigeration – back cooler | 1100 | 2 | 2.2 | 24 | 52.8
Refrigeration – store freezer closed | 1100 | 8 | 8.8 | 2 | 35.2
Refrigeration – store freezer open | 1300 | 3 | 3.9 | 2 | 15.6
Refrigeration – store cooler closed | 1100 | 9 | 9.9 | 2 | 39.6
Refrigeration -Total |  |  | 27.05 |  | 197.2
Lighting – Fluorescent T8 | 32 | 155 | 4.96 | 12 | 59.52
Lighting – LED | 13.5
Lightening - Halogen
Lighting – Total |  |  | 4.96 |  | 59.52
Air Conditioning | 22500 |  | 22.5 | 12 | 270
Cooking | 1782 |  | 1.782 | 2 | 3.564
Water Heating | 1100 |  | 1.1 | 2 | 2.2
ICT – ATM Machine | 700 | 1 | 0.7 | 12 | 8.4
ICT – Computer, Monitor, Printer | 158 | 3 | 0.474 | 12 | 5.69
ICT – Cash Register | 200 | 6 | 1.2 | 12 | 14.4
ICT - Total |  |  | 2.374 |  | 28.49
ACTUAL TOTAL |  |  | 59.8 |  | 561
LIVINCHUN SUPERMARKET
Subject | Power Rating (W) | Amount | Total Power (W)
Refrigeration – back freezer | 1125 | 1 | 1125
Refrigeration – back cooler | 1100 | 1 | 1100
Refrigeration – store freezer closed | 1100 | 9 | 9900
Refrigeration – store freezer open | 1300 | 2 | 2600
Refrigeration – store cooler closed | 1100 | 3 | 3300
Refrigeration -Total |  |  | 18025
Lighting – Fluorescent T8 | 32
Lighting – LED | 13.5
Lightening - Halogen | 60 | 120 | 7200
Lighting – Total |  |  | 7200
Air Conditioning | 5500 |  | 5500
Cooking | 1782 |  | 1782
Water Heating | 1100 |  | 1100
ICT – ATM Machine | 700 | 1 | 700
ICT – Computer, Monitor, Printer | 158 | 2 | 316
ICT – Cash Register | 200 | 4 | 800
ICT - Total |  |  | 1816
ACTUAL TOTAL |  |  | 35423
WELCOME YOU SUPERMARKET
Subject | Power Rating (W) | Amount | Total Power (W)
Refrigeration – back freezer | 1125 | 2 | 2250
Refrigeration – back cooler | 1100 | 1 | 1100
Refrigeration – store freezer closed | 1100 | 5 | 5500
Refrigeration – store freezer open | 1300 | 6 | 7800
Refrigeration – store cooler closed | 1100 | 8 | 8800
Refrigeration -Total |  |  | 25450
Lighting – Fluorescent T8 | 32 | 210 | 6720
Lighting – LED | 13.5
Lightening - Halogen | 60
Lighting – Total |  |  | 6720
Air Conditioning | 4644 |  | 4644
Cooking | 1782 |  | 1782
Water Heating | 1100 |  | 1100
ICT – ATM Machine | 700 | 1 | 700
ICT – Computer, Monitor, Printer | 158 | 5 | 790
ICT – Cash Register | 200 | 6 | 1200
ICT - Total |  |  | 2690
ACTUAL TOTAL |  |  | 44340
CHANRAIS SUPERMARKET
Subject | Power Rating (W) | Amount | Total Power (W)
Refrigeration – back freezer | 1125 | 2 | 2250
Refrigeration – back cooler | 1100 | 4 | 4400
Refrigeration – store freezer closed | 1100 | 1 | 1100
Refrigeration – store freezer open | 1300 | 5 | 6500
Refrigeration – store cooler closed | 1100 | 8 | 8800
Refrigeration -Total |  |  | 23050
Lighting – Fluorescent T8 | 32 | 150 | 4800
Lighting – LED | 13.5
Lightening - Halogen | 60
Lighting – Total |  |  | 4800
Air Conditioning | 9143 |  | 9143
Cooking | 1782 |  | 1782
Water Heating | 1100 |  | 1100
ICT – ATM Machine | 700 | 1 | 700
ICT – Computer, Monitor, Printer | 158 | 3 | 474
ICT – Cash Register | 200 | 5 | 1000
ICT - Total |  |  | 2174
ACTUAL TOTAL |  |  | 42049
EVERYDAY SUPERMARKET
Subject | Power Rating (W) | Amount | Total Power (W)
Refrigeration – back freezer | 1125 | 5 | 5625
Refrigeration – back cooler | 1100 | 2 | 2200
Refrigeration – store freezer closed | 1100 | 3 | 3300
Refrigeration – store freezer open | 1300 | 6 | 7800
Refrigeration – store cooler closed | 1100 | 15 | 16500
Refrigeration -Total |  |  | 35425
Lighting – Fluorescent T8 | 32 | 165 | 5280
Lighting – LED | 13.5 | 56 | 756
Lightening - Halogen
Lighting – Total |  |  | 6036
Air Conditioning | 7815 |  | 7815
Cooking | 1782 |  | 1782
Water Heating | 1100 |  | 1100
ICT – ATM Machine | 700 | 1 | 700
ICT – Computer, Monitor, Printer | 158 | 4 | 632
ICT – Cash Register | 200 | 8 | 1700
ICT - Total |  |  | 3032
ACTUAL TOTAL |  |  | 55190
NEXTIME SUPERMARKET
Subject | Power Rating (W) | Amount | Total Power (W)
Refrigeration – back freezer | 1125 | 4 | 4500
Refrigeration – back cooler | 1100 | 2 | 2200
Refrigeration – store freezer closed | 1100 | 4 | 4400
Refrigeration – store freezer open | 1300 | 7 | 9100
Refrigeration – store cooler closed | 1100 | 6 | 6600
Refrigeration -Total |  |  | 26800
Lighting – Fluorescent T8 | 32 | 250 | 8000
Lighting – LED | 13.5
Lightening - Halogen
Lighting – Total |  |  | 8000
Air Conditioning | 9800 |  | 9800
Cooking | 1782 |  | 1782
Water Heating | 1100 |  | 1100
ICT – ATM Machine | 700 | 1 | 700
ICT – Computer, Monitor, Printer | 158 | 3 | 474
ICT – Cash Register | 200 | 7 | 1400
ICT - Total |  |  | 4290
ACTUAL TOTAL |  |  | 51772
NEXT SUPERMARKET
Subject | Power Rating (W) | Amount | Total Power (W)
Refrigeration – back freezer | 1125 | 6 | 6750
Refrigeration – back cooler | 1100 | 7 | 7700
Refrigeration – store freezer closed | 1100 | 7 | 7700
Refrigeration – store freezer open | 1300 | 1 | 1300
Refrigeration – store cooler closed | 1100 | 2 | 2200
Refrigeration -Total |  |  | 25650
Lighting – Fluorescent T8 | 32 | 110 | 3520
Lighting – LED | 13.5
Lightening - Halogen
Lighting – Total |  |  | 3520
Air Conditioning | 12000 |  | 12000
Cooking | 1782 |  | 1782
Water Heating | 1100 |  | 1100
ICT – ATM Machine | 700 | 1 | 700
ICT – Computer, Monitor, Printer | 158 | 2 | 316
ICT – Cash Register | 200 | 5 | 1000
ICT - Total |  |  | 2016
ACTUAL TOTAL |  |  | 46068