## Table 1 to 3
Table 1. Coefficients of Polynomial Curve Fit for Power vs Dry Bulb Temperature
Coefficients |  | Classroom | Computer Room | Laboratory Room | Office (shared) | Office (solo)
Power vs Dry Bulb Temperature | c1 | 0 | 0 | 0 | 0.0136 | 0.012
| c2 | -0.0023 | -0.0005 | -0.0006 | -0.0124 | -0.0159
| c3 | 0.0693 | 0.1731 | 0.102 | 0.0222 | 0.0261
Table 2. Coefficients of Polynomial Curve Fit for Power vs Relative Humidity
Coefficients |  | Classroom | Computer Room | Laboratory Room | Office (shared) | Office (solo)
Power vs Humidity | c1 | 0.0106 | 0 | 0.0066 | -0.0026 | -0.0023
| c2 | -0.0055 | 0.0022 | -0.0104 | 0.0116 | 0.0113
| c3 | -0.0694 | -0.1478 | -0.0504 | -0.019 | -0.0188
| c4 | 0.1041 | 3.2459 | 0.1266 | 0.0268 | 0.0277
Table 3. Coefficients of Polynomial Curve Fit for Power vs CO2 Levels
Coefficients |  | Classroom | Computer Room | Laboratory Room | Office (shared) | Office (solo)
Power vs Carbon Dioxide Level | c1 | -0.0125 | -0.0007 | -0.0018 | -0.0015 | 0.0002
| c2 | 0.1407 | -0.1682 | 0.1548 | -0.022 | -0.0548

## Table 4 & 5
Table 4. Polynomial Curve of ACU Power using Least Absolute Residuals for Instructional Rooms
Relationship | Classroom |  |  | Computer Room |  |  | Laboratory Room
| Degree | R-square | RMSE | Degree | R-square | RMSE | Degree | R-square | RMSE
P vs T | 1 | 0.9983 | 0.0028 | 1 | 0.9998 | 0.00093718 | 3 | 0.9866 | 0.007
P vs RH | 3 | 0.9881 | 0.0074 | 3 | 0.9991 | 0.0018 | 3 | 0.9813 | 0.0084
P vs CO2 | 1 | 0.987 | 0.0071 | 1 | 0.9967 | 0.0028 | 1 | 0.986 | 0.0074
Table 5. Polynomial Curve of ACU Power using Least Absolute Residuals for Office Spaces
Relationship | Office Space (shared) |  |  | Office space (solo)
| Degree | R-square | RMSE | Degree | R-square | RMSE
P vs T | 2 | 0.9911 | 0.004 | 3 | 0.993 | 0.0036
P vs RH | 3 | 0.992 | 0.0038 | 3 | 0.9899 | 0.0043
P vs CO2 | 1 | 0.9957 | 0.0027 | 1 | 0.9944 | 0.004

## Table 6
Table 6. Neural Fit Test Performances of ACU Power vs Indoor Thermal and Carbon Dioxide Levels
Model Parameters |  | Classroom | Computer Room | Laboratory Room | Office | Office
[5 empty] | (shared) | (solo)
P vs T | Epoch | 24 | 11 | 9 | 12 | 11
| MSE | 0.0042 | 0.0017 | 0.003 | 0.0011 | 0.0011
| R | 0.3037 | 0.7502 | 0.384 | 0.5751 | 0.654
P vs H | Epoch | 11 | 10 | 15 | 13 | 11
| MSE | 0.0028 | 0.0015 | 0.0027 | 0.0011 | 0.0013
| R | 0.6299 | 0.7595 | 0.5395 | 0.6108 | 0.548
P vs CO2 | Epoch | 12 | 8 | 12 | 78 | 41
| MSE | 0.0037 | 0.0011 | 0.001 | 0.0018 | 0.0018
| R | 0.2552 | 0.837 | 0.4603 | 0.196 | 0.0462

## Table 7
Table 78. Steady state power conditions at Stable Thermal and CO2 Levels
Room | ACU Setpoint | Average Power | Dry bulb temperature | Relative Humidity | CO2 Level
| (°C) | (kWh) | (°C) | (%) | (ppm)
Classroom | 23 | 1745.4 | 25.39 | 56.91 | 1335
Computer Room | 23 | 1720.8 | 24.17 | 50.05 | 400
Laboratory Room | 21 | 2030.4 | 22.44 | 37.87 | 1562
Office (shared) | 25 | 1030.8 | 25.2 | 34.96 | 400
Office (solo) | 25 | 1030.8 | 25.39 | 50.32 | 426

## Supplementantal Tables
Table S1. Polynomial Curve Fitting Performance for Instructional Rooms (ACU Power vs Dry Bulb Temperature)
Robustness | Classroom |  |  | Computer Room |  |  | Laboratory Room
| Degree | R-square | RMSE | Degree | R-square | RMSE | Degree | R-square | RMSE
OFF | 9 | 0.0606 | 0.0661 | 9 | 0.5947 | 0.0379 | 9 | 0.1538 | 0.056
LAR | 1 | 0.9983 | 0.0028 | 1 | 0.9998 | 0.00093718 | 3 | 0.9866 | 0.007
Bi-square | 1 | 0.9983 | 0.0028 | 1 | 0.9995 | 0.0013 | 9 | 0.2404 | 0.0531
Table S2. Polynomial Curve Fitting Performance for Office Spaces (ACU Power vs Dry Bulb Temperature)
Robustness | Office Space (shared) |  |  | Office space (solo)
| Degree | R-square | RMSE | Degree | R-square | RMSE
OFF | 9 | 0.3359 | 0.0347 | 9 | 0.384 | 0.0334
LAR | 2 | 0.9911 | 0.004 | 2 | 0.9904 | 0.0042
Bi-square | 3 | 0.8139 | 0.0183 | 8 | 0.8119 | 0.0184
Table S3. Polynomial Curve Fitting Performance for Instructional Rooms (ACU Power vs Relative Humidity)
Robustness | Classroom |  |  | Computer Room |  |  | Laboratory Room
| Degree | R-square | RMSE | Degree | R-square | RMSE | Degree | R-square | RMSE
OFF | 9 | 0.4314 | 0.0515 | 7 | 0.527 | 0.0409 | 9 | 0.2806 | 0.052
LAR | 3 | 0.9881 | 0.0074 | 3 | 0.9991 | 0.0018 | 3 | 0.9813 | 0.0084
Bi-square | 8 | 0.8241 | 0.0286 | 1 | 0.9995 | 0.0014 | 9 | 0.5261 | 0.0422
Table S4. Polynomial Curve Fitting Performance for Office Spaces (ACU Power vs Relative Humidity)
Robustness | Office Space (shared) |  |  | Office space (solo)
| Degree | R-square | RMSE | Degree | R-square | RMSE
OFF | 7 | 0.3819 | 0.0334 | 9 | 0.3125 | 0.0353
LAR | 3 | 0.992 | 0.0038 | 3 | 0.9899 | 0.0043
Bi-square | 6 | 0.8932 | 0.0139 | 3 | 0.8726 | 0.0152
Table S5. Polynomial Curve Fitting Performance for Instructional Rooms (ACU Power vs CO2 level)
Robustness | Classroom |  |  | Computer Room |  |  | Laboratory Room
| Degree | R-square | RMSE | Degree | R-square | RMSE | Degree | R-square | RMSE
OFF | 9 | 0.1207 | 0.0588 | 9 | 0.0201 | 0.0491 | 9 | 0.0568 | 0.061
LAR | 1 | 0.987 | 0.0071 | 1 | 0.9967 | 0.0028 | 1 | 0.986 | 0.0074
Bi-square | 9 | 0.3307 | 0.0031 | 1 | 0.8909 | 0.0163 | 1 | -0.1074 | 0.0659
Table S6. Polynomial Curve Fitting Performance for Office Spaces (ACU Power vs CO2 Level)
Robustness | Office space (shared) |  |  | Office space (solo)
| Degree | R-square | RMSE | Degree | R-square | RMSE
OFF | 9 | 0.0267 | 0.0411 | 9 | 0.0306 | 0.0534
LAR | 1 | 0.9957 | 0.0027 | 1 | 0.9944 | 0.004
Bi-square | 1 | 0.9283 | 0.0111 | 1 | 0.942 | 0.013
Table S7. Neural Fit in ACU Power vs Dry bulb temperature
Model Parameters |  | Classroom | Computer Room | Laboratory Room | Office (shared) | Office (solo)
Epoch |  | 68 | 11 | 9 | 12 | 11
Performance |  | 0.0043 | 0.00136 | 0.00299 | 0.0012 | 0.00112
Validation Checks |  | 6 | 6 | 6 | 6 | 6
Train | Observation | 1637 | 6600 | 1346 | 2526 | 1823
| MSE | 0.0043 | 0.0014 | 0.0031 | 0.0012 | 0.0011
| R | 0.2942 | 0.7792 | 0.4177 | 0.5924 | 0.6114
Validation | Observation | 351 | 1415 | 289 | 542 | 391
| MSE | 0.0043 | 0.0013 | 0.003 | 0.0011 | 0.001
| R | 0.229 | 0.7794 | 0.4921 | 0.5878 | 0.6571
Test | Observation | 351 | 1415 | 289 | 542 | 391
| MSE | 0.0037 | 0.0017 | 0.003 | 0.0011 | 0.0011
| R | 0.3922 | 0.7502 | 0.384 | 0.5751 | 0.654
Table S8. Neural Fit in ACU Power vs Relative Humidity
Model Parameters |  | Classroom | Computer Room | Laboratory Room | Office (shared) | Office (solo)
Epoch |  | 11 | 10 | 15 | 13 | 11
Performance |  | 0.00259 | 0.00175 | 0.00262 | 0.00111 | 0.00119
Validation Checks |  | 6 | 6 | 6 | 6 | 6
Train | Observation | 1607 | 6600 | 1097 | 2526 | 1823
| MSE | 0.0026 | 0.0018 | 0.0026 | 0.0011 | 0.0012
| R | 0.6627 | 0.7179 | 0.5426 | 0.6232 | 0.5741
Validation | Observation | 345 | 1415 | 235 | 542 | 391
| MSE | 0.0026 | 0.0015 | 0.0026 | 0.0011 | 0.0013
| R | 0.6767 | 0.7331 | 0.5476 | 0.6412 | 0.5536
Test | Observation | 345 | 1415 | 235 | 542 | 391
| MSE | 0.0028 | 0.0015 | 0.0027 | 0.0011 | 0.0013
| R | 0.6299 | 0.7595 | 0.5395 | 0.6108 | 0.548
Table S9. Neural Fit in ACU Power vs Carbon Dioxide Level
Model Parameters |  | Classroom | Computer Room | Laboratory Room | Office (shared) | Office (solo)
Epoch |  | 12 | 8 | 12 | 78 | 41
Performance |  | 0.00333 | 0.0011 | 0.00102 | 0.00174 | 0.00177
Validation Checks |  | 6 | 6 | 6 | 1 | 6
Train | Observation | 1198 | 8141 | 1097 | 2526 | 1823
| MSE | 0.0033 | 0.0011 | 0.001 | 0.0017 | 0.0018
| R | 0.2952 | 0.8294 | 0.5458 | 0.16 | 0.1082
Validation | Observation | 257 | 1745 | 235 | 542 | 391
| MSE | 0.0033 | 0.001 | 0.0008 | 0.0018 | 0.0019
| R | 0.2793 | 0.8459 | 0.5721 | 0.2151 | 0.1075
Test | Observation | 0.2608 | 1745 | 235 | 542 | 391
| MSE | 0.0037 | 0.0011 | 0.001 | 0.0018 | 0.0018
| R | 0.2552 | 0.837 | 0.4603 | 0.196 | 0.0462
Table S10. Coefficients of Polynomial Curve Fit for Power vs Temperature and Humidity
Coefficients |  | Instructional Room | Office Space
Power vs Temperature vs Humidity | c1 | 2.9919 | 1.794
| c2 | -0.0924 | -0.0442
| c3 | -0.0512 | -0.0463
| c4 | 0.0014 | 0.0009
| c5 | 0.001 | 0.0002
Table S11. Polynomial Curve of ACU Power using Least Absolute Residuals for Office Spaces
Relationship | Degree |  | Instructional Room |  | Office Space
| T | H | RMSE | Degree | R-square | RMSE
P vs T,H | 1 | 2 | 0.9982 | 0.0026 | 0.9874 | 0.0048